## Summary
VMC
SUMMARY: ELECTRICAL WORKS INSTALLATION - VMC
SECTION | DESCRIPTION | QTY RQD' | AMOUNT | TOTAL
0 | P&G's
1 | HVAC | Lot
2 | WET SERVICES | 1
3 | FIRE SYSTEM | 1
4 | LP GAS INSTALLATION | 1
SUB TOTAL 1
CONTIGENCIES 10%
SUB TOTAL 2
15% VAT
TOTAL BID PRICE VAT INCL

## HVAC
SCHEDULE OF QUANTITIES
MECHANICAL INSTALLATION
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
NO
1 | AIR - CONDITIONING INSTALLATION
1.1. | MIDWALL SPLIT UNITS(CEILING CASSETTES)
1.1.1 | CCU-01 -3.5 kW Ceiling Cassette AC , ceiling cassette unit complete with refrigeration piping, steel brackets and 25mm diameter uPVC condensate drain piping for both indoor and outdoor units. Hand held remote control with wall mounted bracket. | No | 1 | 18500 | 18500
1.1.2 | FCU-01 - 11.0 kW Hideaway Fan Coil Unit, Fan Coil Unit, midwall split unit complete with refrigeration piping, steel brackets and 25mm diameter uPVC condensate drain piping for both indoor and outdoor units. Hand held remote control with wall mounted bracket. | No | 3 | 26000 | 78000
1.1.3 | MW-01 - 4.5 kW midwall split unit complete with refrigeration piping, steel brackets and 25mm diameter uPVC condensate drain piping for both indoor and outdoor units. Hand held remote control with wall mounted bracket. | No | 1 | 16000 | 16000
1.1.4 | Galvanised P7000 trunking for externally mounted refrigeration piping with removable lids, incl bracketing, bends etc. | m | 20 | 350 | 7000
1.1.5 | All electrical works associated with the installation of the outdoor and indoor units that requires such electrical installation for full operation of all systems as per specifications and national regulations. This includes all COC's and compliance with all local and national regulations where required. | Sum | 1 | 15000 | 15000
1.2 | VENTILATION INSTALLATION
1.2.1 | Fresh Air systems
1.2.1.1 | FAF - 01: Inline duct fan (450 l/s @ 200Pa) complete with attenuators, including other connections, hangers, anti-vibration mountings, electrical installation to within 1m of fan, associated timers installation and all other associated installation costs as per drawing and specification. | No | 2 | 15000 | 30000
1.2.2 | Extraction Air systems
SUB-TOTAL CARRIED FORWARD
1.2.1.1 | EAF - 01: ams or other approved inline duct fan (200 l/s @ 200Pa) complete with attenuators, including other connections, hangers, anti-vibration mountings, electrical installation to within 1m of fan, associated timers installation and all other associated installation costs as per drawing and specification. | No | 2 | 15000 | 30000
1.2.1.2 | 9m long Stainless Extraction Canopy | No | 2 | 30000 | 60000
1.2.1.2 | 6m long Stainless Extraction Canopy | No | 2 | 21000 | 42000
1.3 | Ducting
Rigid non-insulated ducting suspended in ceiling space from roof trusses including all straight and round ducting including flanges, hangers, supports, spigots, reductions and mezz flanges. Including acoustic flexible spiral reinforced ducting no longer than 1.5m in length per unit as required for complete installation of duct system per unit as per drawings for:
1.3.1 | FAF - 01 | sum | 1
1.3.2 | EAF - 01 | sum | 1
1.4 | DISC VALVES
1.4.1 | EAV - 01: Ф 200mm DVK valves | no | 4
1.5 | BALANCING DAMPERS
1.5.1 | Supply and install balancing dampers as per drawings and specification | No | 12
SUB-TOTAL CARRIED FORWARD
1.6 | WEATHER LOUVRES
1.6.1 | WL - 01: Weather louvre 600mm x 400mm as per drawing and specification complete with installation costs | No | 1
1.7 | WP77 WASHABLE FILTERS
1.7.1 | Supply and install 600mm x 400mm WP77 washable filter complete with slide in panel and box, as per the drawings and specifications | No | 3
1.8 | DOOR GRILLES
1.8.1 | Supply and install 400mm x 300mm DG type door grilles, as per the drawings | No | 4
1.9 | BUDGETARY ALLOWANCES
1.9.1 | Workshop Drawings | Sum | 1
SUB-TOTAL CARRIED FORWARD
TOTAL FOR THIS SECTION CARRIED FORWARD TO SUMMARY PAGE

## WET SERVICES
Wet Services Installation
BILL NO 1: DRAINAGE
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
1 | Drainage (Below Ground)
Supply and install uPVC CLASS 4 pipes (below ground waste) according to the specifications and drawings, complete with brackets, clamps and hangers.
Piping
1.1 | Ø50 mm | m | 50
1.2 | Ø110 mm | m | 100
PVC Fittings
BENDS
1.3 | Ø50 mm (88.5°) | qty | 15
1.4 | Ø110 mm (88.5°) | qty | 6
1.5 | Ø50 mm (45°) | qty | 13
1.6 | Ø110 mm (45°) | qty | 8
45° Junctions
1.7 | Ø50 - Ø50 - Ø50 mm | qty | 8
1.8 | Ø110 - 110- 110 mm | qty | 6
1.8 | Ø110 - 110- 50 mm | qty | 4
Pipe Accessories
1.7 | Rodding Eye | qty | 2
2 | Domestic Cold and Hot (At High Level)
Copper pipes (at high level) according to the specifications and drawings, complete with brackets, clamps and hangers.
Piping
2.1 | Ø15 mm | m | 50
2.2 | Ø22 mm | m | 25
2.2 | Ø28 mm | m | 2
2.2 | Ø42 mm | m | 20
Bends
2.1 | Ø15 mm | qty | 32
2.2 | Ø22 mm | qty | 22
2.3 | Ø28 mm | qty | 0
2.4 | Ø35 mm | qty | 6
Reducing Tees
2.5 | Ø15 - Ø15- Ø15 mm | qty | 3
2.6 | Ø22 - Ø22- Ø15 mm | qty | 4
2.7 | Ø22 - Ø22- Ø22 mm | qty | 5
2.8 | Ø28 - Ø28- Ø22 mm | qty | 2
2.8 | Ø35 - Ø35- Ø35 mm | qty | 2
Reducers
2.9 | Ø15 - Ø15 mm | qty | 9
2.10 | Ø15 - Ø22 mm | qty | 5
2.11 | Ø22 - Ø28 mm | qty | 3
2.12 | Ø22 - Ø35 mm | qty | 3
Plumbing Fixtures
2.13 | 10 Litres Under-counter sink | qty | 2
Insulation (Themaflex 15mm)
Supply and Install Insulation on all Copper hot water piping in ceiling
2.14 | Ø15 mm | m | 20
2.15 | Ø22 mm | m | 0
Ball-O-Stop Valves
2.16 | Ø15 mm | m | 5
2.17 | Ø22 mm | m | 12
STORAGE TANKS AND PUMPS
| Supply and install a 5 000 litres vertical Jojo pvc tank mounted on a concrete plinth and install complete with all valve accessories. | sum | 1
| Allow for connection of the Jojo tank to the water reticulation for domestic use. | sum | 1
| 1.5 l/s @ 4.5 bars domestic water pumps duty and standby are required to be installed complete with the necessary suction/ delivery pipework, valves, control equipment, pressure switches control panel and pressure vessel. | sum | 1
| Supply and install 150L solar Geyer | sum | 1
0

## FIRE SYTERM
SCHEDULE OF QUANTITIES
SECTION NO.3 FIRE SYTERM
ITEM | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
NO | CLAUSE
SECTION NO.3 FIRE SYTERM
TWIN BOOSTER CONNECTION AND FIRE WATER RETICULATION PIPING
All equipment as per SABS approved standards:
|  | All costs for connecting, delivery, fittings, connections and hanging materials to be included. | No. | 1
|  | booster connection, twin brass 65mm with pressure gauge, glycerine filled 2500kPA | No. | 1
|  | valve, non return 100mm including threaded/flange connections/joints | No. | 2
|  | valve, butterfly 100mm including threaded/flange connections/joints | No. | 1
Connect to existing Fire mains
|  | Water meter for hydrant/hose reel system includingthreaded/flange connections/joints | No. | 1
Below ground piping
HDPE PN12 with fusion welded fittings installed underground, not deeper than 1m. Trenches and backfilling to be included, installed as per SANS 10252 and manufacturers specifications
|  | below ground pipe 110mm | M | 30
|  | below ground pipe 32mm | M | 20
HDPE Fittings Fusion welded:
|  | Hydrant Tee (Flanged) Diameter 100mm | No. | 1
|  | Equal Tee Diameter 110mm | No. | 2
|  | 900 Bend Tee Diameter 110mm | No. | 2
|  | 900 Bend Tee Diameter 32mm | No. | 4
|  | 100mm to 50mm Reducer | No. | 2
|  | 50mm to 32mm Reducer | No. | 2
|  | Transformation from HDPE to Steel Diameter 100mm | No. | 1
|  | Transformation from HDPE to Steel Diameter 32mm | No. | 2
Above ground piping
Black Mild Steel BS62 installed as per SANS 10252 and manufacturers specifications
|  | pipe, med m/s 100mm | M | 5
|  | pipe, med m/s 32mm | M | 5
|  | painting 100mm pipe, as per specification | M | 5
|  | painting 32mm pipe, as per specification | M | 5
FIRE HYDRANTS
All equipment as per SABS approved standards.
All costs for connecting, delivery, fittings, connections and hanging materials to be included.
|  | hydrant landing valve, brass 100mm | No. | 1
|  | pressure gauge, glycerine filled 1000kPA | No. | 1
FIRE HOSE REELS
All costs for connecting, delivery, fittings, connections and hanging materials to be included.
|  | fire hose reel, c/w 30m hose to EN694 standard | No. | 2
|  | pressure gauge, glycerine filled 1000kPA | No. | 2
|  | weatherproof fire hose reel cabinet | No. | 2
PORTABLE FIRE EXTINGUISHERS
All equipment as per SABS approved standards.
All extinguishers to include mounting brackets.
|  | extinguisher, 4,5kg DCP | No. | 12
|  | extinguisher, 5kg CO2 | No. | 2
TESTING AND COMMISSION
|  | Testing and commission, incl. all labour | Sum | 1
BILL NO.2: SINAGES
STATUTORY SIGNAGE
Supply and installation of aluminium framed SABS 1186 approved photoluminescent type signage, as detailed below:
|  | running man + down arrow | no | 3
- Code E3
- single sided, 190 x 190mm
- white lettering
- green background
|  | running man + left arrow | no | 2
- Code E2
- single sided, 190 x 190mm
- white lettering
- green background
|  | running man + right arrow | no | 2
- Code E1
- single sided
- white lettering
- green background
|  | hose reel + extinguisher + down arrow | no | 2
- Code F4
- single sided, 190 x 190mm
- red lettering
- white background
|  | hydrant + down arrow | no | 1
- Code F15
- single sided, 190 x 190mm
- red lettering
- white background
|  | extinguisher + down arrow | no | 3
- Code F13
- single sided, 190 x 190mm
- red lettering
- white background
|  | EXIT | no | 1
- Code E6
- green lettering
- white background
|  | 110mm diameter floor drain. | No | 6
FIRE BOOSTER PUMPS
|  | Installation and erection of a pump set consisting of 2-off inline vertical electric pumps multi-stage centrifugal booster pumps or approved equivalent pump set capable of delivering a total of 1,5 litres per second of clean water @ 6bars each c/w VSD drives | SUM | 1
Pumps to be installed c/w equipment listed below:
|  | • Jockey pump | No. | 1
|  | • Ø65mm Strainers | No. | 2
|  | • Ø65mm Non-return valves | No. | 2
|  | • Ø65mm Isolating butterfly valves | No. | 4
|  | • Pressure gauges | No. | 2
|  | • EP8 pressure switch c/w isolating valves | No. | 2
|  | • Dry run float switch | No. | 1
|  | • IP54 Control panel c/w alarm | No. | 1
|  | • Galvanized inlet manifold | No. | 1
|  | • Galvanized outlet manifold | No. | 1
|  | • 80 mm Bi-level control valve to be fitted to elevated tank inlet | No. | 1
|  | • Electrical Wiring to control panel | m | 18
|  | •Controls | Item | 1
•Supports, anti-vibration mountings and other fixing
|  | accessories | Item | 1
|  | • O & M Manuals | No. | 3
• All the above mounted on a base, pre-piped, pre-wired and
|  | tested | Item | 1
FIRE WATER TANK
|  | 147 000 Litres steel panel tank supported on concrete plinth 600mm above the ground c/w with all fittings. | Item | 1
TOTAL | [5 empty] | 0

## LP Gas
SCHEDULE OF QUANTITIES
SECTION NO.4 LP GAS INSTALLATION
ITEM | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
NO | CLAUSE
SECTION NO.4 LP GAS INSTALLATION
LP GAS INSTALLATION
All equipment as per SABS 10087 approved standards:
|  | LP Gas installation complete with piping , supports and gas cylinders. | Item | 1
TOTAL | [5 empty] | 0